## Head Vs. Flow
updated 2/5/05

## Pipe Loss Regression
ft/sec | vel^2 |  | loss
10.9 | 118.81 |  | 0.926
11.9 | 141.61 |  | 1.1 |  | SUMMARY OUTPUT
12.9 | 166.41 |  | 1.28
13.8 | 190.44 |  | 1.48 |  | Regression Statistics
14.8 | 219.04 |  | 1.69 |  | Multiple R | 0.99995
17.3 | 299.29 |  | 2.29 |  | R Square | 0.9999
19.8 | 392.04 |  | 2.97 |  | Adjusted R Square | 0.92848
22.2 | 492.84 |  | 3.75 |  | Standard Error | 0.035027
24.7 | 610.09 |  | 4.61 |  | Observations | 15
27.2 | 739.84 |  | 5.56
29.7 | 882.09 |  | 6.6 |  | ANOVA
32.1 | 1030.41 |  | 7.73 |  |  | df | SS | MS | F | Significance F
34.6 | 1197.16 |  | 8.95 |  | Regression | 1 | 179.9627 | 179.9627 | 146679.2462 | 9.8998e-28
37.1 | 1376.41 |  | 10.3 |  | Residual | 14 | 0.017177 | 0.0012269
39.5 | 1560.25 |  | 11.7 |  | Total | 15 | 179.9799
|  |  |  | loss in feet |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
|  | v for 30" | v^2 | of head | Intercept | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
180 | cfs | 39.9273 | 1594.1854 | 11.9625 | X Variable 1 | 0.0075038 | 1.1577e-05 | 648.1496 | 9.5604e-33 | 0.007479 | 0.0075287 | 0.007479 | 0.0075287
170 | cfs | 37.7091 | 1421.974 | 10.6702
160 | cfs | 35.4909 | 1259.6033 | 9.4518
150 | cfs - exactly | 33.2727 | 1107.0732 | 8.3073
144 | cfs | 31.9418 | 1020.2787 | 7.656
140 | cfs | 31.0545 | 964.3838 | 7.2366
130 | cfs | 28.8363 | 831.535 | 6.2397
120 | cfs | 26.6182 | 708.5269 | 5.3167
110 | cfs -exactly | 24.4 | 595.3594 | 4.4675
100 | cfs | 22.1818 | 492.0325 | 3.6921
90 | cfs | 19.9636 | 398.5464 | 2.9906
80 | cfs | 17.7454 | 314.9008 | 2.363
70 | cfs | 15.5273 | 241.0959 | 1.8091

## Pipe analysis
Rock Creek Retrofit Project
assumed pipe diameter |  | 30 | inches nominal 28.75 ID
[9 empty] | New Steel Pipe | [5 empty] | Hydro | Head
Gross head |  | 87.75 | feet - max | [5 empty] | Pipe loss Table |  |  | Turbine efficiency |  |  | (From PG&E)
pipe length |  | 90 | feet - 30" | [5 empty] | 30 " steel pipe |  |  | Estimation w/w |  |  | Oper Pt. | Max
Entrance condition |  | rough filleted | [6 empty] | ft/sec | ft loss/100' |  | 95% | gen |  | 2201 | 2205
Butterfly valves |  | 2 | [6 empty] | 10.9 | 0.926 |  | 97% | gear |  | 2113.25 | 2113.25
90 degree bends |  | 0 | [6 empty] | 11.9 | 1.1 |  | 84% | turbine |  | 87.75 | 91.75
45 degree bends |  | 1 | [6 empty] | 12.9 | 1.28 |  | 77.41% | net efficiency
[9 empty] | 13.8 | 1.48
[9 empty] | 14.8 | 1.69
Trash rack loss |  | 0.9 | feet | expected to vary from 6" to 2' |  |  |  |  | 17.3 | 2.29
Entrance head loss |  | 0.35 | k | Filleted Radius |  |  |  |  | 19.8 | 2.97
Butterfly v. losses |  | 50000 | Cv | Crane - 30" 200 series |  |  |  |  | 22.2 | 3.75
45 degree elbow loss |  | 0.18 | k | Cameron Hydraulic Data by Ing. Rand Page 3-113 |  |  |  |  | 24.7 | 4.61
Bifurcation loss |  | 0.25 | k | Cameron Hydraulic Data by Ing. Rand Page 3-114 |  |  |  |  | 27.2 | 5.56
90 degree loss |  | 0.2 | [6 empty] | 29.7 | 6.6
draft tube recover eff. |  | 75% | estimated | including static and velocity head |  |  |  |  | 32.1 | 7.73
Assumed water-wire |  | 77.41% | constant | assuming 100% draft tube efficiency (see calcs) |  |  |  |  | 34.6 | 8.95
efficiency | including control valve |  |  | assuming inclusive of control valve |  |  |  |  | 37.1 | 10.3
|  |  |  | (check measurement basis) |  |  |  |  | 39.5 | 11.7
Total K |  | 0.78 | Includes: | entrance, bifrucation, 45 elboe
Pipe Area |  | 4.5082 | square feet
Draft tube exit area |  | 12 | square feet
[6 empty] | Double | Draft tube | Draft tube |  | Pipe loss | Loss with |  | draft tube |  |  |  | Equal Power curves for plotting - includes Efficiency
|  |  |  | Pipe | Pipe | butterfly | Exit | exit v^2/2g | total | from table | 17 % rust for |  | loss+
| Flow |  |  | velocity | v^2/2g | loss | velocity | K. energy | (k) losses | for 100' | 90 |  | exit K.E. | net head | kW | efficiency > | 77.41% | 77.41% | 77.41% | 77.41% | 77.41%
| Duration | flow |  | ft/sec | feet | feet | ft/sec | feet | feet | feet | feet |  | feet | feet |  | kW > | 450 | 500 | 550 | 600 | 400
| 80% | 180 | cfs | 39.9273 | 24.7544 | 11.5247 | 15 | 3.4938 | 19.3085 | 11.9625 | 12.5965 |  | 8.8089 | 34.6114 | 407.9775 | 3.5739 | 38.1764 | 42.4182 | 46.66 | 50.9019 | 33.9346
|  | 170 | cfs | 37.7091 | 22.0803 | 10.2798 | 14.1667 | 3.1164 | 17.2227 | 10.6702 | 11.2358 |  | 7.8574 | 40.2544 | 448.1336 | 3.9257 | 40.4221 | 44.9134 | 49.4048 | 53.8961 | 35.9307
|  | 160 | cfs | 35.4909 | 19.5591 | 9.106 | 13.3333 | 2.7605 | 15.2561 | 9.4518 | 9.9528 |  | 6.9602 | 45.575 | 477.5204 | 4.1831 | 42.9485 | 47.7205 | 52.4926 | 57.2646 | 38.1764
| 10% | 150 | cfs - exactly | 33.2727 | 17.1906 | 8.0033 | 12.5 | 2.4262 | 13.4087 | 8.3073 | 8.7476 |  | 6.1173 | 50.5732 | 496.7712 | 4.3517 | 45.8117 | 50.9019 | 55.9921 | 61.0822 | 40.7215
|  | 140 | cfs | 31.0545 | 14.9749 | 6.9717 | 11.6667 | 2.1135 | 11.6804 | 7.2366 | 7.6201 |  | 5.3289 | 55.2488 | 506.5196 | 4.4371 | 49.0839 | 54.5377 | 59.9915 | 65.4453 | 43.6302
|  | 130 | cfs | 28.8363 | 12.912 | 6.0114 | 10.8333 | 1.8224 | 10.0714 | 6.2397 | 6.5704 |  | 4.5948 | 59.6021 | 507.3991 | 4.4448 | 52.8596 | 58.7329 | 64.6062 | 70.4795 | 46.9863
|  | 120 | cfs | 26.6182 | 11.002 | 5.1221 | 10 | 1.5528 | 8.5815 | 5.3167 | 5.5984 |  | 3.9151 | 63.6328 | 500.0431 | 4.3804 | 57.2646 | 63.6273 | 69.9901 | 76.3528 | 50.9019
| 10% | 110 | cfs -exactly | 24.4 | 9.2447 | 4.304 | 9.1667 | 1.3048 | 7.2109 | 4.4675 | 4.7042 |  | 3.2898 | 67.3411 | 485.0852 | 4.2493 | 62.4705 | 69.4116 | 76.3528 | 83.294 | 55.5293
|  | 100 | cfs | 22.1818 | 7.6403 | 3.557 | 8.3333 | 1.0783 | 5.9594 | 3.6921 | 3.8878 |  | 2.7188 | 70.727 | 463.1589 | 4.0573 | 68.7175 | 76.3528 | 83.9881 | 91.6234 | 61.0822
|  | 90 | cfs | 19.9636 | 6.1886 | 2.8812 | 7.5 | 0.87345 | 4.8271 | 2.9906 | 3.1491 |  | 2.2022 | 73.7903 | 434.8976 | 3.8097 | 76.3528 | 84.8365 | 93.3201 | 101.8037 | 67.8692
|  | 80 | cfs | 17.7454 | 4.8898 | 2.2765 | 6.6667 | 0.69013 | 3.814 | 2.363 | 2.4882 |  | 1.74 | 76.5313 | 400.9349 | 3.5122 | 85.8969 | 95.441 | 104.9851 | 114.5292 | 76.3528
|  | 70 | cfs | 15.5273 | 3.7437 | 1.7429 | 5.8333 | 0.52838 | 2.9201 | 1.8091 | 1.905 |  | 1.3322 | 78.9497 | 361.9042 | 3.1703 | 98.1679 | 109.0754 | 119.983 | 130.8905 | 87.2604
***********************************************************************************************************
note head to centerline
[5 empty] | Straight Pipe Analysis | [6 empty] | 2202 | water height |  | 2202 | head
Pipe Exit total gross head |  | 47.75 | gross feet of head |  |  |  | Study of the Existing Exit |  |  |  |  | 1.5 | centerline correction |  | 2113.25 | tail water
Trash Rack Loss |  | 1.375 | foot - trash rack loss ( measured) | [8 empty] | 2152.75 | exit elevation (checked) |  | 88.75 | gross head
[12 empty] | 47.75 | drop to exit pipe
Entrance Loss |  | 0.57 | k | square edges on outward curved surface
45 degree elbow loss |  | 0.18 | k | Cameron Hydraulic Data by Ing. Rand Page 3-113 - each
Total K |  | 0.93 | Includes: | entrance, + 2 45 degree elboes
[12 empty] | 2113.25 | tailwater
Butterfly v. losses |  | 50000 | Cv | ELY estimate | [7 empty] | 39.5 | drop left plus exit velocity
|  | 73426 | from crane | Crane - 30" 200 series use for |  |  | 2 Butterfly valves
Pipe Area |  | 4.5082 | square feet | assumes 28.75" inside diameter
Pipe Length |  | 73 | feet | [6 empty] | Pipe loss
from table
for 100'
|  |  |  | Pipe | Pipe head | Cv derived | k of .25 loss |  |  | calculated
|  |  |  | velocity | v^2/2g | Double Butterfly loss | (Alternate)Double Butterfly loss |  | Total k type losses | by regression | Pipe Loss for 73' + 17% for rust |  | Total head friction loss | net head after friction | exit K.E. | balance head at output orifice
|  | FLOW |  | ft/sec | feet | feet | feet |  | feet | feet | in feet |  |  | feet | feet
|  | 180 | cfs | 39.9273 | 24.7544 | 11.4961 | 12.3772 |  | 23.0216 | 11.9625 | 10.2172 |  | 46.1099 | 1.6401 | 24.7544 | -23.1143
|  | 170 | cfs | 37.7091 | 22.0803 | 10.2542 | 11.0402 |  | 20.5347 | 10.6702 | 9.1135 |  | 41.2774 | 6.4726 | 22.0803 | -15.6078
|  | 160 | cfs | 35.4909 | 19.5591 | 9.0833 | 9.7795 |  | 18.1899 | 9.4518 | 8.0728 |  | 36.7211 | 11.0289 | 19.5591 | -8.5301
|  | 150 | cfs - exactly | 33.2727 | 17.1906 | 7.9834 | 8.5953 |  | 15.9872 | 8.3073 | 7.0953 |  | 32.4409 | 15.3091 | 17.1906 | -1.8815
|  | 144 | cfs | 31.9418 | 15.8428 | 7.3575 | 7.9214 |  | 14.7338 | 7.656 | 6.539 |  | 30.0053 | 17.7447 | 15.8428 | 1.9018 | <<<<<-----
|  | 140 | cfs | 31.0545 | 14.9749 | 6.9544 | 7.4875 |  | 13.9267 | 7.2366 | 6.1808 |  | 28.4368 | 19.3132 | 14.9749 | 4.3383
|  | 130 | cfs | 28.8363 | 12.912 | 5.9964 | 6.456 |  | 12.0082 | 6.2397 | 5.3293 |  | 24.7089 | 23.0411 | 12.912 | 10.129
|  | 120 | cfs | 26.6182 | 11.002 | 5.1094 | 5.501 |  | 10.2318 | 5.3167 | 4.541 |  | 21.2572 | 26.4928 | 11.002 | 15.4909
|  | 110 | cfs -exactly | 24.4 | 9.2447 | 4.2933 | 4.6224 |  | 8.5976 | 4.4675 | 3.8157 |  | 18.0815 | 29.6685 | 9.2447 | 20.4237
|  | 100 | cfs | 22.1818 | 7.6403 | 3.5482 | 3.8201 |  | 7.1054 | 3.6921 | 3.1534 |  | 15.1821 | 32.5679 | 7.6403 | 24.9277
|  | 90 | cfs | 19.9636 | 6.1886 | 2.874 | 3.0943 |  | 5.7554 | 2.9906 | 2.5543 |  | 12.5587 | 35.1913 | 6.1886 | 29.0027
|  | 80 | cfs | 17.7454 | 4.8898 | 2.2708 | 2.4449 |  | 4.5475 | 2.363 | 2.0182 |  | 10.2115 | 37.5385 | 4.8898 | 32.6487
|  | 70 | cfs | 15.5273 | 3.7437 | 1.7386 | 1.8719 |  | 3.4817 | 1.8091 | 1.5452 |  | 8.1405 | 39.6095 | 3.7437 | 35.8658
[6 empty] | 2 valves | 2 valves
Probably High
OK for small valves
Ignorred

## Sample Turbines
Sample 36" Fancis
| head | flow
| 85 | 100
| 80 | 96.5
| 78 | 94.9
| 75 | 93
| 70 | 90.7